## ConexionDB
Name | IP | Port | Bucket | Organization | Token
Test | host.docker.internal | 8086 | Laboratorio_Energias | USC | 4pJB_298afu0WKjKBtPESjnUxvpJV0PODWBNMGzeeU_ahg1P4H3Bg5KOfwI2A9LXm2BQwaQR_un792HXy3bsvg==

## ConexionAnalizadores
Name | IP | Port
Totalizador_Lovato | 172.16.219.135 | 501

## Cargas
Unit ID | Name | Analyzer
1 | TP_Totalizador | Totalizador_Lovato
2 | TP_Sistema PBM | Totalizador_Lovato
3 | TP_Analizador Biogas | Totalizador_Lovato
4 | TP_Planta de Biogas | Totalizador_Lovato
5 | TP_Tunel de viento - Potencia | Totalizador_Lovato
6 | TP_Ventilador sistema eolico | Totalizador_Lovato
7 | TP_Torre de enfriamiento | Totalizador_Lovato
8 | TP_Banco de trabajo turbinas | Totalizador_Lovato
9 | TP_Tablero Paneles | Totalizador_Lovato
10 | TP_Iluminacion Biogas | Totalizador_Lovato
11 | TP_Video Wall Smart Grid | Totalizador_Lovato
12 | TP_Iluminacion fotovoltaico | Totalizador_Lovato
13 | TP_Video Controller Smart Grid | Totalizador_Lovato
14 | TP_Iluminacion Smartgrid | Totalizador_Lovato
15 | TP_Mesa Biogas Fotovoltaico | Totalizador_Lovato
16 | TP_Nevera Biogas | Totalizador_Lovato
17 | TP_Meson Sala Biogas | Totalizador_Lovato
18 | TP_Tunel de viento - control | Totalizador_Lovato
19 | TP_Modulo fotovoltaico eolico | Totalizador_Lovato
20 | TP_Modulo control turbinas | Totalizador_Lovato

## Variables
Address Hex | Address Dec | Word | Description | Unit | Format | Scale | Name | field
0x0002 | 2 | 2 | L1 Phase Voltage | V | Unsigned | 100 | L1 Voltaje | V-001
0x0004 | 4 | 2 | L2 Phase Voltage | V | Unsigned | 100 | L2 Voltaje | V-002
0x0006 | 6 | 2 | L3 Phase Voltage | V | Unsigned | 100 | L3 Voltaje | V-003
0x0008 | 8 | 2 | L1 Current | A | Unsigned | 10000 | L1 Corriente | I-001
0x000A | 10 | 2 | L2 Current | A | Unsigned | 10000 | L2 Corriente | I-002
0x000C | 12 | 2 | L3 Current | A | Unsigned | 10000 | L3 Corriente | I-003
0x000E | 14 | 2 | L1-L2 Voltage | V | Unsigned | 100 | L1-L2 Voltaje | V-012
0x0010 | 16 | 2 | L2-L3 Voltage | V | Unsigned | 100 | L2-L3 Voltaje | V-023
0x0012 | 18 | 2 | L3-L1 Voltage | V | Unsigned | 100 | L3-L1 Voltaje | V-031
0x0014 | 20 | 2 | L1 Active Power | kW | Signed | 100000 | L1 Potencia Activa | P-001
0x0016 | 22 | 2 | L2 Active Power | kW | Signed | 100000 | L2 Potencia Activa | P-002
0x0018 | 24 | 2 | L3 Active Power | kW | Signed | 100000 | L3 Potencia Activa | P-003
0x001A | 26 | 2 | L1 Reactive Power | kvar | Signed | 100000 | L1 Potencia Reactiva | Q-001
0x001C | 28 | 2 | L2 Reactive Power | kvar | Signed | 100000 | L2 Potencia Reactiva | Q-002
0x001E | 30 | 2 | L3 Reactive Power | kvar | Signed | 100000 | L3 Potencia Reactiva | Q-003
0x0020 | 32 | 2 | L1 Apparent Power | kVA | Unsigned | 100000 | L1 Potencia Aparente | S-001
0x0022 | 34 | 2 | L2 Apparent Power | kVA | Unsigned | 100000 | L2 Potencia Aparente | S-002
0x0024 | 36 | 2 | L3 Apparent Power | kVA | Unsigned | 100000 | L3 Potencia Aparente | S-003
0x0026 | 38 | 2 | L1 Power Factor |  | Signed | 10000 | L1 Factor de Potencia | FP-001
0x0028 | 40 | 2 | L2 Power Factor |  | Signed | 10000 | L2 Factor de Potencia | FP-002
0x002A | 42 | 2 | L3 Power Factor |  | Signed | 10000 | L3 Factor de Potencia | FP-003
0x0032 | 50 | 2 | Frequency | Hz | Unsigned | 1000 | Frecuencia | FREQ
0x0034 | 52 | 2 | Eqv Phase Voltage | V | Unsigned | 100 | Voltaje Equivalente LN | VN-123
0x0036 | 54 | 2 | Eqv Phase-To-Phase Voltage | V | Unsigned | 100 | Voltaje Equivalente LL | V-123
0x0038 | 56 | 2 | Eqv Current | A | Unsigned | 10000 | Corriente Equivalente | I-123
0x003A | 58 | 2 | Eqv Active Power | kW | Signed | 100000 | Total Potencia Activa | P-123
0x003C | 60 | 2 | Eqv Reactive Power | kvar | Signed | 100000 | Total Potencia Reactiva | Q-123
0x003E | 62 | 2 | Eqv Apparent Power | kVA | Unsigned | 100000 | Total Potencia Aparente | S-123
0x0040 | 64 | 2 | Eqv Power Factor |  | Signed | 10000 | Total Factor de Potencia | FP-123
0x0042 | 66 | 2 | VLL Unbalance | % | Unsigned | 100 | Desbalance de Voltaje LN | VNU-123
0x0044 | 68 | 2 | VLN Unbalance | % | Unsigned | 100 | Desbalance de Voltaje LL | VU-123
0x0046 | 70 | 2 | Current Unbalance | % | Unsigned | 100 | Desbalance de Corriente | IU-123
0x0054 | 84 | 2 | Thd L1 Voltage | % | Unsigned | 100 | L1 THD Voltaje | V1-THD
0x0056 | 86 | 2 | Thd L2 Voltage | % | Unsigned | 100 | L2 THD Voltaje | V2-THD
0x0058 | 88 | 2 | Thd L3 Voltage | % | Unsigned | 100 | L3 THD Voltaje | V3-THD
0x005A | 90 | 2 | THD L1 Current | % | Unsigned | 100 | L1 THD Corriente | I1-THD
0x005C | 92 | 2 | THD L2 Current | % | Unsigned | 100 | L2 THD Corriente | I2-THD
0x005E | 94 | 2 | THD L3 Current | % | Unsigned | 100 | L3 THD Corriente | I3-THD
0x0C00 | 3072 | 2 | Harmonic 2 VL1 | % | Unsigned | 100 | L1 Armónico Voltaje 2 | V1-H02
0x0C02 | 3074 | 2 | Harmonic 3 VL1 | % | Unsigned | 100 | L1 Armónico Voltaje 3 | V1-H03
0x0C04 | 3076 | 2 | Harmonic 4 VL1 | % | Unsigned | 100 | L1 Armónico Voltaje 4 | V1-H04
0x0C06 | 3078 | 2 | Harmonic 5 VL1 | % | Unsigned | 100 | L1 Armónico Voltaje 5 | V1-H05
0x0C08 | 3080 | 2 | Harmonic 6 VL1 | % | Unsigned | 100 | L1 Armónico Voltaje 6 | V1-H06
0x0C0A | 3082 | 2 | Harmonic 7 VL1 | % | Unsigned | 100 | L1 Armónico Voltaje 7 | V1-H07
0x0C0C | 3084 | 2 | Harmonic 8 VL1 | % | Unsigned | 100 | L1 Armónico Voltaje 8 | V1-H08
0x0C0E | 3086 | 2 | Harmonic 9 VL1 | % | Unsigned | 100 | L1 Armónico Voltaje 9 | V1-H09
0x0C10 | 3088 | 2 | Harmonic 10 VL1 | % | Unsigned | 100 | L1 Armónico Voltaje 10 | V1-H10
0x0C12 | 3090 | 2 | Harmonic 11 VL1 | % | Unsigned | 100 | L1 Armónico Voltaje 11 | V1-H11
0x0C14 | 3092 | 2 | Harmonic 12 VL1 | % | Unsigned | 100 | L1 Armónico Voltaje 12 | V1-H12
0x0C16 | 3094 | 2 | Harmonic 13 VL1 | % | Unsigned | 100 | L1 Armónico Voltaje 13 | V1-H13
0x0C18 | 3096 | 2 | Harmonic 14 VL1 | % | Unsigned | 100 | L1 Armónico Voltaje 14 | V1-H14
0x0C1A | 3098 | 2 | Harmonic 15 VL1 | % | Unsigned | 100 | L1 Armónico Voltaje 15 | V1-H15
0x0C40 | 3136 | 2 | Harmonic 2 VL2 | % | Unsigned | 100 | L2 Armónico Voltaje 2 | V2-H02
0x0C42 | 3138 | 2 | Harmonic 3 VL2 | % | Unsigned | 100 | L2 Armónico Voltaje 3 | V2-H03
0x0C44 | 3140 | 2 | Harmonic 4 VL2 | % | Unsigned | 100 | L2 Armónico Voltaje 4 | V2-H04
0x0C46 | 3142 | 2 | Harmonic 5 VL2 | % | Unsigned | 100 | L2 Armónico Voltaje 5 | V2-H05
0x0C48 | 3144 | 2 | Harmonic 6 VL2 | % | Unsigned | 100 | L2 Armónico Voltaje 6 | V2-H06
0x0C4A | 3146 | 2 | Harmonic 7 VL2 | % | Unsigned | 100 | L2 Armónico Voltaje 7 | V2-H07
0x0C4C | 3148 | 2 | Harmonic 8 VL2 | % | Unsigned | 100 | L2 Armónico Voltaje 8 | V2-H08
0x0C4E | 3150 | 2 | Harmonic 9 VL2 | % | Unsigned | 100 | L2 Armónico Voltaje 9 | V2-H09
0x0C50 | 3152 | 2 | Harmonic 10 VL2 | % | Unsigned | 100 | L2 Armónico Voltaje 10 | V2-H10
0x0C52 | 3154 | 2 | Harmonic 11 VL2 | % | Unsigned | 100 | L2 Armónico Voltaje 11 | V2-H11
0x0C54 | 3156 | 2 | Harmonic 12 VL2 | % | Unsigned | 100 | L2 Armónico Voltaje 12 | V2-H12
0x0C56 | 3158 | 2 | Harmonic 13 VL2 | % | Unsigned | 100 | L2 Armónico Voltaje 13 | V2-H13
0x0C58 | 3160 | 2 | Harmonic 14 VL2 | % | Unsigned | 100 | L2 Armónico Voltaje 14 | V2-H14
0x0C5A | 3162 | 2 | Harmonic 15 VL2 | % | Unsigned | 100 | L2 Armónico Voltaje 15 | V2-H15
0x0C80 | 3200 | 2 | Harmonic 2 VL3 | % | Unsigned | 100 | L3 Armónico Voltaje 2 | V3-H02
0x0C82 | 3202 | 2 | Harmonic 3 VL3 | % | Unsigned | 100 | L3 Armónico Voltaje 3 | V3-H03
0x0C84 | 3204 | 2 | Harmonic 4 VL3 | % | Unsigned | 100 | L3 Armónico Voltaje 4 | V3-H04
0x0C86 | 3206 | 2 | Harmonic 5 VL3 | % | Unsigned | 100 | L3 Armónico Voltaje 5 | V3-H05
0x0C88 | 3208 | 2 | Harmonic 6 VL3 | % | Unsigned | 100 | L3 Armónico Voltaje 6 | V3-H06
0x0C8A | 3210 | 2 | Harmonic 7 VL3 | % | Unsigned | 100 | L3 Armónico Voltaje 7 | V3-H07
0x0C8C | 3212 | 2 | Harmonic 8 VL3 | % | Unsigned | 100 | L3 Armónico Voltaje 8 | V3-H08
0x0C8E | 3214 | 2 | Harmonic 9 VL3 | % | Unsigned | 100 | L3 Armónico Voltaje 9 | V3-H09
0x0C90 | 3216 | 2 | Harmonic 10 VL3 | % | Unsigned | 100 | L3 Armónico Voltaje 10 | V3-H10
0x0C92 | 3218 | 2 | Harmonic 11 VL3 | % | Unsigned | 100 | L3 Armónico Voltaje 11 | V3-H11
0x0C94 | 3220 | 2 | Harmonic 12 VL3 | % | Unsigned | 100 | L3 Armónico Voltaje 12 | V3-H12
0x0C96 | 3222 | 2 | Harmonic 13 VL3 | % | Unsigned | 100 | L3 Armónico Voltaje 13 | V3-H13
0x0C98 | 3224 | 2 | Harmonic 14 VL3 | % | Unsigned | 100 | L3 Armónico Voltaje 14 | V3-H14
0x0C9A | 3226 | 2 | Harmonic 15 VL3 | % | Unsigned | 100 | L3 Armónico Voltaje 15 | V3-H15
0x0CC0 | 3264 | 2 | Harmonic 1 I1 | % | Unsigned | 100 | L1 Armónico Corriente 1 | I1-H01
0x0CC2 | 3266 | 2 | Harmonic 2 I1 | % | Unsigned | 100 | L1 Armónico Corriente 2 | I1-H02
0x0CC4 | 3268 | 2 | Harmonic 3 I1 | % | Unsigned | 100 | L1 Armónico Corriente 3 | I1-H03
0x0CC6 | 3270 | 2 | Harmonic 4 I1 | % | Unsigned | 100 | L1 Armónico Corriente 4 | I1-H04
0x0CC8 | 3272 | 2 | Harmonic 5 I1 | % | Unsigned | 100 | L1 Armónico Corriente 5 | I1-H05
0x0CCA | 3274 | 2 | Harmonic 6 I1 | % | Unsigned | 100 | L1 Armónico Corriente 6 | I1-H06
0x0CCC | 3276 | 2 | Harmonic 7 I1 | % | Unsigned | 100 | L1 Armónico Corriente 7 | I1-H07
0x0CCE | 3278 | 2 | Harmonic 8 I1 | % | Unsigned | 100 | L1 Armónico Corriente 8 | I1-H08
0x0CD0 | 3280 | 2 | Harmonic 9 I1 | % | Unsigned | 100 | L1 Armónico Corriente 9 | I1-H09
0x0CD2 | 3282 | 2 | Harmonic 10 I1 | % | Unsigned | 100 | L1 Armónico Corriente 10 | I1-H10
0x0CD4 | 3284 | 2 | Harmonic 11 I1 | % | Unsigned | 100 | L1 Armónico Corriente 11 | I1-H11
0x0CD6 | 3286 | 2 | Harmonic 12 I1 | % | Unsigned | 100 | L1 Armónico Corriente 12 | I1-H12
0x0CD8 | 3288 | 2 | Harmonic 13 I1 | % | Unsigned | 100 | L1 Armónico Corriente 13 | I1-H13
0x0CDA | 3290 | 2 | Harmonic 14 I1 | % | Unsigned | 100 | L1 Armónico Corriente 14 | I1-H14
0x0CDC | 3292 | 2 | Harmonic 15 I1 | % | Unsigned | 100 | L1 Armónico Corriente 15 | I1-H15
0x0D00 | 3328 | 2 | Harmonic 1 I2 | % | Unsigned | 100 | L2 Armónico Corriente 1 | I2-H01
0x0D02 | 3330 | 2 | Harmonic 2 I2 | % | Unsigned | 100 | L2 Armónico Corriente 2 | I2-H02
0x0D04 | 3332 | 2 | Harmonic 3 I2 | % | Unsigned | 100 | L2 Armónico Corriente 3 | I2-H03
0x0D06 | 3334 | 2 | Harmonic 4 I2 | % | Unsigned | 100 | L2 Armónico Corriente 4 | I2-H04
0x0D08 | 3336 | 2 | Harmonic 5 I2 | % | Unsigned | 100 | L2 Armónico Corriente 5 | I2-H05
0x0D0A | 3338 | 2 | Harmonic 6 I2 | % | Unsigned | 100 | L2 Armónico Corriente 6 | I2-H06
0x0D0C | 3340 | 2 | Harmonic 7 I2 | % | Unsigned | 100 | L2 Armónico Corriente 7 | I2-H07
0x0D0E | 3342 | 2 | Harmonic 8 I2 | % | Unsigned | 100 | L2 Armónico Corriente 8 | I2-H08
0x0D10 | 3344 | 2 | Harmonic 9 I2 | % | Unsigned | 100 | L2 Armónico Corriente 9 | I2-H09
0x0D12 | 3346 | 2 | Harmonic 10 I2 | % | Unsigned | 100 | L2 Armónico Corriente 10 | I2-H10
0x0D14 | 3348 | 2 | Harmonic 11 I2 | % | Unsigned | 100 | L2 Armónico Corriente 11 | I2-H11
0x0D16 | 3350 | 2 | Harmonic 12 I2 | % | Unsigned | 100 | L2 Armónico Corriente 12 | I2-H12
0x0D18 | 3352 | 2 | Harmonic 13 I2 | % | Unsigned | 100 | L2 Armónico Corriente 13 | I2-H13
0x0D1A | 3354 | 2 | Harmonic 14 I2 | % | Unsigned | 100 | L2 Armónico Corriente 14 | I2-H14
0x0D1C | 3356 | 2 | Harmonic 15 I2 | % | Unsigned | 100 | L2 Armónico Corriente 15 | I2-H15
0x0D40 | 3392 | 2 | Harmonic 1 I3 | % | Unsigned | 100 | L3 Armónico Corriente 1 | I3-H01
0x0D42 | 3394 | 2 | Harmonic 2 I3 | % | Unsigned | 100 | L3 Armónico Corriente 2 | I3-H02
0x0D44 | 3396 | 2 | Harmonic 3 I3 | % | Unsigned | 100 | L3 Armónico Corriente 3 | I3-H03
0x0D46 | 3398 | 2 | Harmonic 4 I3 | % | Unsigned | 100 | L3 Armónico Corriente 4 | I3-H04
0x0D48 | 3400 | 2 | Harmonic 5 I3 | % | Unsigned | 100 | L3 Armónico Corriente 5 | I3-H05
0x0D4A | 3402 | 2 | Harmonic 6 I3 | % | Unsigned | 100 | L3 Armónico Corriente 6 | I3-H06
0x0D4C | 3404 | 2 | Harmonic 7 I3 | % | Unsigned | 100 | L3 Armónico Corriente 7 | I3-H07
0x0D4E | 3406 | 2 | Harmonic 8 I3 | % | Unsigned | 100 | L3 Armónico Corriente 8 | I3-H08
0x0D50 | 3408 | 2 | Harmonic 9 I3 | % | Unsigned | 100 | L3 Armónico Corriente 9 | I3-H09
0x0D52 | 3410 | 2 | Harmonic 10 I3 | % | Unsigned | 100 | L3 Armónico Corriente 10 | I3-H10
0x0D54 | 3412 | 2 | Harmonic 11 I3 | % | Unsigned | 100 | L3 Armónico Corriente 11 | I3-H11
0x0D56 | 3414 | 2 | Harmonic 12 I3 | % | Unsigned | 100 | L3 Armónico Corriente 12 | I3-H12
0x0D58 | 3416 | 2 | Harmonic 13 I3 | % | Unsigned | 100 | L3 Armónico Corriente 13 | I3-H13
0x0D5A | 3418 | 2 | Harmonic 14 I3 | % | Unsigned | 100 | L3 Armónico Corriente 14 | I3-H14
0x0D5C | 3420 | 2 | Harmonic 15 I3 | % | Unsigned | 100 | L3 Armónico Corriente 15 | I3-H15
0x1B20 | 6943 | 4 | Active Energy - Import | kWh | Unsigned | 100 | Total Energía Activa - Importación | EAI-123
0x1B28 | 6951 | 4 | Reactive Energy - Import | kvarh | Unsigned | 100 | Total Energía Reactiva - Importación | ERI-123
0x1B2C | 6955 | 4 | Reactive Energy - Export | kvarh | Signed | 100 | Total Energía Reactiva - Exportación | ERE-123
0x1B30 | 6959 | 4 | Apparent Energy | kVAh | Unsigned | 100 | Total Energía Aparente | EAP-123
0x1B98 | 7063 | 4 | L1 Active Energy - Import | kWh | Unsigned | 100 | L1 Energía Activa - Importación | EAI-001
0x1BA0 | 7071 | 4 | L1 Reactive Energy - Import | kvarh | Unsigned | 100 | L1 Energía Reactiva - Importación | ERI-001
0x1BA4 | 7075 | 4 | L1 Reactive Energy - Export | kvarh | Unsigned | 100 | L1 Energía Reactiva - Exportación | ERE-001
0x1BA8 | 7079 | 4 | L1 Apparent Energy | kVAh | Unsigned | 100 | L1 Energía Aparente | EAP-001
0x1BAC | 7083 | 4 | L2 Active Energy - Import | kWh | Unsigned | 100 | L2 Energía Activa - Importación | EAI-002
0x1BB4 | 7091 | 4 | L2 Reactive Energy - Import | kvarh | Unsigned | 100 | L2 Energía Reactiva - Importación | ERI-002
0x1BB8 | 7095 | 4 | L2 Reactive Energy - Export | kvarh | Unsigned | 100 | L2 Energía Reactiva - Exportación | ERE-002
0x1BBC | 7099 | 4 | L2 Apparent Energy | kVAh | Unsigned | 100 | L2 Energía Aparente | EAP-002
0x1BC0 | 7103 | 4 | L3 Active Energy - Import | kWh | Unsigned | 100 | L3 Energía Activa - Importación | EAI-003
0x1BC8 | 7111 | 4 | L3 Reactive Energy - Import | kvarh | Unsigned | 100 | L3 Energía Reactiva - Importación | ERI-003
0x1BCC | 7115 | 4 | L3 Reactive Energy - Export | kvarh | Unsigned | 100 | L3 Energía Reactiva - Exportación | ERE-003
0x1BD0 | 7119 | 4 | L3 Apparent Energy | kVAh | Unsigned | 100 | L3 Energía Aparente | EAP-003
0x1800 | 6144 | 2 | Dip |  | Unsigned | 1 |  | DIP
0x1802 | 6146 | 2 | Swell |  | Unsigned | 1 |  | SWELL
0x1804 | 6148 | 2 | Interruptions |  | Unsigned | 1 |  | INTER
0x1806 | 6150 | 2 | Interruptions > 180S |  | Unsigned | 1 |  | INTER180
0x1808 | 6152 | 2 | Voltage variation NHI |  | Unsigned | 1 |  | VV-NHI
0x180A | 6154 | 2 | Voltage variation HI |  | Unsigned | 1 |  | VV-HI
0x180C | 6156 | 2 | Voltage variation NLOW |  | Unsigned | 1 |  | VV-NLOW
0x180E | 6158 | 2 | Voltage variation LOW |  | Unsigned | 1 |  | VV-LOW
0x1810 | 6160 | 2 | THD |  | Unsigned | 1 |  | THD-EV
0x1812 | 6162 | 2 | Asymmetry |  | Unsigned | 1 |  | ASYMM
0x1814 | 6164 | 2 | Frequency variation NHI |  | Unsigned | 1 |  | FV-NHI
0x1816 | 6166 | 2 | Frequency variation HI |  | Unsigned | 1 |  | FV-HI
0x1818 | 6168 | 2 | Frequency variation NLOW |  | Unsigned | 1 |  | FV-NLOW
0x181A | 6170 | 2 | Frequency variation LOW |  | Unsigned | 1 |  | FV-LOW
0x181C | 6172 | 2 | Harmonics |  | Unsigned | 1 |  | HARMO
0x33E0 | 13280 | 1 | Overvoltage (Weekly) | % | Unsigned | 10 |  | OV-WEEK
0x33E1 | 13281 | 1 | Undervoltage (Weekly) | % | Unsigned | 10 |  | UV-WEEK
0x33E2 | 13282 | 1 | Voltage asymmetry (Weekly) | % | Unsigned | 10 |  | VAS-WEEK
0x33E3 | 13283 | 1 | Overfrequency (Weekly) | % | Unsigned | 10 |  | OF-WEEK
0x33E4 | 13284 | 1 | Underfrequency (Weekly) | % | Unsigned | 10 |  | UF-WEEK
0x33E5 | 13285 | 1 | Voltage THD (Weekly) | % | Unsigned | 10 |  | VTHD-WEEK
0x33E6 | 13286 | 1 | Voltage single harmonics (Weekly) | % | Unsigned | 10 |  | VSH-WEEK
0x3770 | 14192 | 1 | Overvoltage (Yearly) | % | Unsigned | 10 |  | OV-YEAR
0x3771 | 14193 | 1 | Undervoltage (Yearly) | % | Unsigned | 10 |  | UV-YEAR
0x3772 | 14194 | 1 | Voltage THD (Yearly) | % | Unsigned | 10 |  | VTHD-YEAR
0x3773 | 14195 | 1 | Voltage asymmetry (Yearly) | % | Unsigned | 10 |  | VAS-YEAR
0x3774 | 14196 | 1 | Overfrequency (Yearly) | % | Unsigned | 10 |  | OF-YEAR
0x3775 | 14197 | 1 | Underfrequency (Yearly) | % | Unsigned | 10 |  | UF-YEAR
0x3776 | 14198 | 1 | Voltage single harmonics (Yearly) | % | Unsigned | 10 |  | VSH-YEAR
Note on C1: Eros Escobar: 2 = 16 bit 4 = 32 bit